Monitoring:

With integrated monitoring module, for operation on a 24V power supply system. Automatic test system in accordance with DIN EN 62034 type ER, in conjunction with a CoreCompact system. Functions must be complied with:

* Integrated individual luminaire monitoring
* Automatic addressing via configuration wizard
* Luminaires can be individually programmed and dimmed with RP's central power supply system
* Luminaire update via the system

Material: Zinc die-cast

Color: RAL 7016

Dimensions: 55 mm x 193 mm x 120 mm

Diameter: mm

Mounting method: Wandaufbau

Protection class: 2

Protection rating (IP): IP 40

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 15m m

Pictogram: Set

Power maintained mode: 1,7 W W

Power non-maintained mode: 0,4 W W

Input voltage AC: 24 V V

Connection terminals: 2.5 mm² mm

Battery:

Article number: AIW509CC-AZ

Accessories:

Brand: RP-Technik GmbH