Robust safety luminaire made of die-cast zinc for wall mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838  
  
Properties:  
- Mechanically robust and corrosion-resistant  
- Powder-coated surface  
- Exact edges and straight lines  
- No weld seams and bending edges  
- Modern lighting technology  
  
Possible applications are:  
- Open areas, escape route crossings  
- High rooms, warehouses  
- Distance luminaire - luminaire up to 25m  
  
Suitable for continuous or stand-by operation.

Material: Zinc die-cast

Color: RAL 9003

Dimensions: 58 mm x 262 mm x 188 mm

Mounting method: Decke

Protection class: 3

Protection rating (IP): 65

Impact restistence rate IK: 8

Allowed temperature DS: -5 to 40 °C

Allowed temperature BS: -5 to 40 °C

Pictogram: No

Power maintained mode: 3,8 W

Power non-maintained mode: 0,4 W

Luminous Flux Emergency Operation: 520 lm

Bridging time (h): CPS

Input voltage AC: 24 V

Connection terminals: 2.5 mm

Battery:

Article number: FMDS529CC

Accessories:

Article number: FMDA001, ceiling bracket, single sided white

Article number: FMDA002, ceiling bracket, double sided white

Article number: FMDA001-AZ, ceiling bracket, single sided black

Article number: FMDA002-AZ, ceiling bracket, double sided white

Article number: FMWA001, Surface mounting adapter for lateral cable feed

Article number: FMFH, flexible wall mounting for FM

Brand: RP-Technik