Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Slim, elegant, convexe, synthetic luminaire tilted towards the viewer, continuously symmetrically tapered towards the bottom. For universal mounting (wall/ceiling surface mount/integrated ceiling Mount\*/brackets\*). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling mounting or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolfree and variable, use of the pictograms on-site. Set of pictograms (left, right, bottom, top) is included in the scope of delivery.
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

\*With additional adapter

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Plastic

Color: RAL 9003

Dimensions: 34 mm x 250 mm x 174 mm

Diameter: mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): IP 43

Impact restistence rate IK: IK 3

Allowed temperature DS: -5 °C to 35 °C °C

Allowed temperature BS: -5 °C to 35 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 3,9 W W

Power non-maintained mode: 1,5 W W

Luminous Flux Emergency Operation: 190 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery:

Article number: KMU411WL

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: KME-EB, KM recessed frame with test button (SB) ABS white for KM, KSU, KSC, KMB

Article number: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU

Article number: 2PW-EB

Article number: KMBE, concrete recessed housing for KME

Article number: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC

Brand: RP-Technik GmbH