Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
   
Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling Mount\*/brackets\*). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, use of the pictograms on-site. Set of pictograms (left, right, bottom, top) is included in the scope of delivery.   
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

Material: Plastic

Color: RAL 9003

Dimensions: 34 mm x 250 mm x 174 mm

Diameter: mm

lbl-mountingMethod: Universal

lbl-protectionClass: 2

lbl-protectionRating: IP 54

lbl-impactResistanceRate: IK ≥ 3

Allowed temperature DS: -30 °C to 40 °C °C

Allowed temperature BS: -30 °C to 40 °C °C

Viewing distance: 22m m

Pictogram: Set

Power maintained mode: 3,2 W W

Power non-maintained mode: 1 W W

Luminous Flux Emergency Operation: 220 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery:

lbl-articleNumber: KSC019

Accessories:

lbl-articleNumber: DSA, cord suspension set 1,5m

lbl-articleNumber: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU

lbl-articleNumber: 2PW-EB

lbl-articleNumber: KMBE, concrete recessed housing for KME

lbl-articleNumber: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC

lbl-articleNumber: KS4FIRE, Pictoset Fire Fighting \*NEUTRAL\* 2x 4 pictograms for KS, KSC, KBM, SD, RM, AM, AS

lbl-articleNumber: KS4HELP, Pictoset First Aid \*NEUTRAL\* 2x 4 pictograms for KS, KSC, KBM, SD, RM, AM, AS

Brand: RP-Technik GmbH