Emergency luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 und DIN EN 1838.

Emergency luminaire in a sleek Aluminium profile, matt andonized for ceiling mounting with an additional light source to light the Floor below the luminaire. Housing is openable toollessly. Applicable for maintained or non-maintained operation. The toolless change and variable use of the pictograms provide planning security on site.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Aluminum

Color: Alu eloxiert

Dimensions: 62 mm x 614 mm x 334 mm

Diameter: mm

Mounting method: Decke

Protection class: 1

Protection rating (IP): IP 40

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 56m m

Pictogram: Einzeln n.A.

Power maintained mode: 3,2 W W

Power non-maintained mode: 0,9 W W

Battery: LFP3212.K-SET-2AKKU, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

Article number: LSD413SC

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: 2PS-EB

Brand: RP-Technik GmbH