Emergency luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 und DIN EN 1838.   
  
Emergency luminaire in a sleek Aluminium profile, matt andonized for wall mounting with an additional light source to light the Floor below the luminaire. Housing is openable toollessly. Applicable for maintained or non-maintained operation. The toolless change and variable use of the pictograms provide planning security on site. Pluggable set of pictograms (left, right, down, up) is included in the scope of delivery.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Aluminum

Color: Alu eloxiert

Dimensions: 62 mm x 614 mm x 334 mm

Diameter: mm

Mounting method: Wand

Protection class: 1

Protection rating (IP): IP 40

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 56m m

Pictogram: Einzeln n.A.

Power maintained mode: 3,2 W W

Power non-maintained mode: 0,9 W W

Battery: LFP3212.K-SET-2AKKU, LiFePO4 Battery

Article number: LSW411SC

Accessories:

Brand: RP-Technik GmbH