Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838  
   
Plastic luminaire for ceiling mounting. With trapezoidally tapered bonnet secured with screws.  
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Plastic

Color: RAL 9003

Dimensions: 152 mm x 370 mm x 195 mm

Diameter: mm

Mounting method: Deckenaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 6

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 3,3 W W

Power non-maintained mode: 0,9 W W

Luminous Flux Emergency Operation: 190 lm lm

Battery: LFP3216-SET-2AKKU

Article number: PFD411SC

Accessories:

Article number: 2PW-EB

Article number: 2DW-EB

Article number: DSA, cord suspension set 1,5m

Article number: PFER, PF recessed frame for wall / ceiling

Brand: RP-Technik GmbH