Escape sign/safety luminaire in accordance with DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Plastic luminaire for wall or ceiling mounting, with bonnet secured by screws.
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Plastic

Color: RAL 9003

Dimensions: 370 mm x 105 mm x 152 mm

Diameter: mm

Mounting method: Universal

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 5

Allowed temperature DS: -15 °C to 40 °C °C

Allowed temperature BS: -15 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 5,9 W W

Power non-maintained mode: 0,9 W W

Luminous Flux Emergency Operation: 520 lm lm

Battery:

Article number: PFW423SC-TT

Accessories:

Article number: BALL2, Ball protection (8W) 450x280x125mm RAL9010, for KCW, KL, LX, VX, PFW

Brand: RP-Technik GmbH