Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
  
Cube plastic luminaire with frameless bonnet and easy-to-mount bayonet catch. Due to the stable construction, the luminaire can also be suspended by chain or rope.   
  
Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom) as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Plastic

Color: RAL 9003

Dimensions: 500 mm x 522 mm x 280 mm

Diameter: mm

Mounting method: Deckenaufbau

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -15 °C to 40 °C °C

Allowed temperature BS: -15 °C to 40 °C °C

Viewing distance: 50m m

Pictogram: Set

Power maintained mode: 7 W W

Power non-maintained mode: 2 W W

Battery:

Article number: WHGD411SC-TT

Accessories:

Article number: DSA-Y4M, Y wire suspension 4m as a set suitable for cube liuminaires Two-point attachment to the ceiling with transverse anchors, four-point attachment to the luminaire.

Article number: DSA-Y4M-APA, 4m cable suspension incl. mounting plate

Article number: WKO, Set out of 4 x chain eyelet for cube luminaires

Brand: RP-Technik GmbH