Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
  
Cube plastic luminaire with frameless bonnet and easy-to-mount bayonet catch. Due to the stable construction, the luminaire can also be suspended by chain or rope.   
  
Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom) as standard.

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Plastic

Color: RAL 9003

Dimensions: 300 mm x 300 mm x 179.5 mm

Diameter: mm

Mounting method: Decke

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK 4

Allowed temperature DS: 0 °C to 40 °C °C

Allowed temperature BS: 0 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 5,7 W W

Power non-maintained mode: 0,8 W W

Luminous Flux Emergency Operation: 520 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: LFP3233-SET-2AKKU

Article number: WHXD413WL

Accessories:

Article number: WKO, Set out of 4 x chain eyelet for cube luminaires

Article number: DSA-Y4M, Y wire suspension 4m as a set suitable for cube liuminaires Two-point attachment to the ceiling with transverse anchors, four-point attachment to the luminaire.

Article number: DSA-Y4M-APA, 4m cable suspension incl. mounting plate

Brand: RP-Technik GmbH