Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
  
Cube plastic luminaire with frameless bonnet and easy-to-mount bayonet catch. Due to the stable construction, the luminaire can also be suspended by chain or rope.   
  
Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom) as standard.

Monitoring:

With integrated monitoring module, for operation on a 24V power supply system. Automatic test system in accordance with DIN EN 62034 type ER, in conjunction with a CoreCompact system. Functions must be complied with:

* Integrated individual luminaire monitoring
* Automatic addressing via configuration wizard
* Luminaires can be individually programmed and dimmed with RP's central power supply system
* Luminaire update via the system

Material: Plastic

Color: RAL 9003

Dimensions: 300 mm x 300 mm x 179.5 mm

Diameter: mm

Mounting method: Decke

Protection class: 3

Protection rating (IP): IP 65

Impact restistence rate IK: IK 4

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 5,1 W W

Power non-maintained mode: 0,4 W W

Luminous Flux Emergency Operation: 520 lm lm

Input voltage AC: 24 V V

Connection terminals: 2.5 mm² mm

Battery:

Article number: WHXD519CC

Accessories:

Article number: WKO, Set out of 4 x chain eyelet for cube luminaires

Article number: DSA-Y4M, Y wire suspension 4m as a set suitable for cube liuminaires Two-point attachment to the ceiling with transverse anchors, four-point attachment to the luminaire.

Article number: DSA-Y4M-APA, 4m cable suspension incl. mounting plate

Brand: RP-Technik GmbH