Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22

Cube plastic luminaire with frameless bonnet and concealed mounting tray made of galvanised sheet steel.

Suitable for continuous or stand-by operation. Planning reliability due to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top) as standard.

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Metal

Color: RAL 9003

Dimensions: 500 mm x 500 mm x 500 mm

Diameter: mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 20

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 90m m

Pictogram: Set

Power maintained mode: 5,1 W W

Power non-maintained mode: 0,8 W W

Luminous Flux Emergency Operation: 470 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: LFP3216-SET-2AKKU

Article number: WKW411WL

Accessories:

Article number: WKO, Set out of 4 x chain eyelet for cube luminaires

Brand: RP-Technik GmbH