Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Cube plastic luminaire with frameless bonnet and concealed mounting tray made of galvanised sheet steel. Due to the stable construction, the luminaire can also be suspended by chain or rope.

Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms in accordance with DIN EN ISO 7010 and DIN ISO 3864 (left, right, top) as standard.

Material: Metal

Color: RAL 9003

Dimensions: 500 mm x 500 mm x 500 mm

Diameter: mm

Mounting method: Decke

Protection class: 1

Protection rating (IP): IP 20

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -25 °C to 40 °C °C

Allowed temperature BS: -25 °C to 40 °C °C

Viewing distance: 90m m

Pictogram: Set

Power maintained mode: 3,9 W W

Power non-maintained mode: 0 W W

Luminous Flux Emergency Operation: 300 lm lm

Input voltage AC: 230 V V

Connection terminals: 1.5 mm² mm

Battery:

Article number: WXD029

Accessories:

Article number: WKO, Set out of 4 x chain eyelet for cube luminaires

Article number: 1PV-EB

Brand: RP-Technik GmbH