Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Cube plastic luminaire with frameless bonnet and concealed mounting tray made of galvanised sheet steel. Due to the stable construction, the luminaire can also be suspended by chain or rope.

Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms in accordance with DIN EN ISO 7010 and DIN ISO 3864 (left, right, top) as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Metal

Color: RAL 9003

Dimensions: 500 mm x 500 mm x 500 mm

Diameter: mm

Mounting method: Deckenaufbau

Protection class: 1

Protection rating (IP): IP 20

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 90m m

Pictogram: Set

Power maintained mode: 7 W W

Power non-maintained mode: 2 W W

Luminous Flux Emergency Operation: 470 lm lm

Battery: LFP3233-SET-2AKKU

Article number: WXD413SC

Accessories:

Article number: LFP3233-SET-2AKKU

Brand: RP-Technik GmbH